## Form
|  | Blue Solar charge controller MPPT |  |  |  |  | Voltage window |  | Current window
5
| Module: | 17
| In series: | 3 |  | Parallel: | 5
| Total PV power: | 4500 | Wp
|  |  | 15 |  | 0
| Module temperature: | Min. | -10 | Max. | 70 |  |  | 2.5
[7 empty] | 12 | 4
| Controller: | 8 |  |  |  |  | 24 | 6
[7 empty] | 36 | 10
| System voltage: |  | 4 | Volt |  |  | 48 | 25
| Cable length, Module to MPPT * |  | 5 | Cross-section: | 6 | 3
* One way length
| Max. input voltage |  |  | 150
| Max. PV voltage @ min. temperature |  |  | 148.0437
| Min. input voltage @ MPP |  |  | 49
| Min. PV voltage @ max. temperature |  |  | 85.5081
| Max. output current |  |  | 85
| Max. current @ MPP min. temp. |  |  | 85
* Power limiting @ low temp.
| Max. current @ MPP max. temp. |  |  | 75.842
| Solar module configuration |  |  | Accepted | Accepted | NOT accepted
BHO 06-2015 2.0
Are the solar modules covered with snow many periods a year? | [5 empty] | No | FALSE
Example locations with expected temperatures: |  |  |  |  | Min. | Max.
Flat on mobile home, all year (poor ventilation) |  |  |  |  | 0 | 70
Flat on mobile home, only summer (poor ventilation) |  |  |  |  | 15 | 70
Flat on boat (poor ventilation) |  |  |  |  | 10 | 65
Pitched on boat (good ventilation) |  |  |  |  | 5 | 60
Pitched roof in warm region (good ventilation) |  |  |  |  | 5 | 70
Pitched roof in average region (good ventilation) |  |  |  |  | 0 | 65
Pitched roof on mountain (good ventilation) |  |  |  |  | -5 | 60

## Modules
| Manufacturer | Type | Power | Vmpp | Impp | Voc | Isc | V temp coeff | I temp coeff | Art.Nr.
| [name] | [name] | [W] | [V] | [A] | [V] | [A] | [%/°C] | [%/°C]
Victron Energy SPM30-12 (SPM010301200) | Victron Energy | SPM30-12 | 30 | 18 | 1.67 | 22.5 | 2 | -0.34 | 0.037 | SPM010301200
Victron Energy SPM50-12 (SPM010501210) | Victron Energy | SPM50-12 | 50 | 18 | 2.78 | 22.2 | 3.16 | -0.34 | 0.037 | SPM010501210
Victron Energy SPM80-12 (SPM010801210) | Victron Energy | SPM80-12 | 80 | 18 | 4.45 | 22.3 | 4.96 | -0.34 | 0.037 | SPM010801210
Victron Energy SPM100-12 (SPM011001210) | Victron Energy | SPM100-12 | 100 | 18 | 5.56 | 22.4 | 6.53 | -0.34 | 0.037 | SPM011001210
Victron Energy SPM130-12 (SPM011301210) | Victron Energy | SPM130-12 | 130 | 18 | 7.23 | 22.4 | 8.49 | -0.34 | 0.05 | SPM011301210
Victron Energy SPM190-24 (SPM011902400) | Victron Energy | SPM190-24 | 190 | 36 | 5.44 | 43.2 | 5.98 | -0.34 | 0.037 | SPM011902400
Victron Energy SPM300-24 (SPM013002400) | Victron Energy | SPM300-24 | 300 | 36 | 8.06 | 45.5 | 8.56 | -0.34 | 0.037 | SPM013002400
Victron Energy SPP30-12 (SPP010301200) | Victron Energy | SPP30-12 | 30 | 18 | 1.72 | 22.5 | 1.85 | -0.34 | 0.045 | SPP010301200
Victron Energy SPP40-12 (SPP020401200) | Victron Energy | SPP40-12 | 40 | 18 | 2.22 | 22.5 | 1.85 | -0.34 | 0.037 | SPP020401200
Victron Energy SPP50-12 (SPP010501210) | Victron Energy | SPP50-12 | 50 | 18 | 2.85 | 22.2 | 3.09 | -0.34 | 0.037 | SPP010501210
Victron Energy SPP75-12 (SPP020751200) | Victron Energy | SPP75-12 | 75 | 18 | 4.17 | 22.2 | 4.64 | -0.34 | 0.037 | SPP020751200
Victron Energy SPP80-12 (SPP010801210) | Victron Energy | SPP80-12 | 80 | 18 | 4.6 | 21.6 | 5.06 | -0.34 | 0.037 | SPP010801210
Victron Energy SPP100-12 (SPP011001210) | Victron Energy | SPP100-12 | 100 | 18 | 5.75 | 21.6 | 6.32 | -0.34 | 0.037 | SPP011001210
Victron Energy SPP140-12 (SPP011401200) | Victron Energy | SPP140-12 | 140 | 18 | 8.05 | 21.6 | 8.85 | -0.35 | 0.037 | SPP011401200
Victron Energy SPP250-20 (SPP022502400) | Victron Energy | SPP250-20 | 250 | 30 | 8.33 | 36.01 | 9.4 | -0.35 | 0.037 | SPP022502400
Victron Energy SPP280-24 (SPP012802400) | Victron Energy | SPP280-24 | 280 | 36 | 7.78 | 44.06 | 8.26 | -0.34 | 0.045 | SPP012802400
Victron Energy SPP300-24 (SPP023002400) | Victron Energy | SPP300-24 | 300 | 36 | 8.33 | 44.1 | 8.85 | -0.34 | 0.045 | SPP023002400
Custom: 1XYZ 1ABC | Custom: 1XYZ | 1ABC | 50 | 30.89 | 8.9 | 38.2 | 9.52 | -0.31 | 0.047
Custom: 2XYZ 2ABC | Custom: 2XYZ | 2ABC | 75 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 3XYZ 3ABC | Custom: 3XYZ | 3ABC | 100 | 40.2 | 6.46 | 48 | 8.5 | -0.33 | 0.06
Custom: 4XYZ 4ABC | Custom: 4XYZ | 4ABC | 125 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 5XYZ 5ABC | Custom: 5XYZ | 5ABC | 150 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 6XYZ 6ABC | Custom: 6XYZ | 6ABC | 175 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 7XYZ 7ABC | Custom: 7XYZ | 7ABC | 200 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 8XYZ 8ABC | Custom: 8XYZ | 8ABC | 225 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 9XYZ 9ABC | Custom: 9XYZ | 9ABC | 250 | 35.5 | 6.46 | 45 | 8.5 | -0.33 | 0.06
Custom: 10XYZ 10ABC | Custom: 10XYZ | 10ABC | 275 | 44.3 | 5.54 | 53 | 5.86 | -0.25 | 0.03
Coefficient support:
If you have the voltage temperature coefficient in mV/°C, here is how to change it to %/°C
Write the Voc value in Volt: |  | 24.1 | V
Write the coefficient value in mV/°C: |  | -77 | mV/°C
The coefficent value in %/°C is now: |  | -0.3195 | %/°C
If you have the current temperature coefficient in mA/°C, here is how to change it to %/°C
Write the Isc value in Ampere: |  | 8.72 | A
Write the coefficient value in mA/°C: |  | 4.7 | mA/°C
The coefficent value in %/°C is now: |  | 0.053899 | %/°C

## Regulator
| Manufacturer | Type | Power @ 12V | Power @ 24V | Power @ 36V | Power @ 48V | Voc max | Voc min | Vmpp min | System Voltage |  |  |  | Ibat max | Efficiency@12 | Efficiency@24 | Efficiency@36 | Efficiency@48
Victron Energy BlueSolar MPPT 75/10 | Victron Energy | BlueSolar MPPT 75/10 | 135 | 270 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 10 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 75/15 | Victron Energy | BlueSolar MPPT 75/15 | 200 | 400 | 0 | 0 | 75 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 100/15 | Victron Energy | BlueSolar MPPT 100/15 | 200 | 400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 15 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 100/30 | Victron Energy | BlueSolar MPPT 100/30 | 440 | 880 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 30 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 100/50 | Victron Energy | BlueSolar MPPT 100/50 | 700 | 1400 | 0 | 0 | 100 | 5 | 1 | 12 | 24 | N.A. | N.A. | 50 | 0.98 | 0.98 | 0 | 0
Victron Energy BlueSolar MPPT 150/35 | Victron Energy | BlueSolar MPPT 150/35 | 500 | 1000 | 1500 | 2000 | 150 | 5 | 1 | 12 | 24 | 36 | 48 | 35 | 0.98 | 0.98 | 0.98 | 0.98
Victron Energy BlueSolar MPPT 150/70 | Victron Energy | BlueSolar MPPT 150/70 | 1000 | 2000 | 3000 | 4000 | 150 | 7 | 2 | 12 | 24 | 36 | 48 | 70 | 0.95 | 0.965 | 0.97 | 0.975
Victron Energy BlueSolar MPPT 150/85 | Victron Energy | BlueSolar MPPT 150/85 | 1200 | 2400 | 3600 | 4850 | 150 | 7 | 2 | 12 | 24 | 36 | 48 | 85 | 0.95 | 0.965 | 0.97 | 0.975

## Calculation table
DATA:
Location: | -10 | min
| 70 | max
Module info: | 132.3 | Voc @25°C
| 108 | Vmpp @25°C
| 44.25 | Isc PV@25°C
| 41.65 | Impp PV @25°C
| 93.7125 | Impp output @25°C
| -0.34 | Temp. Coeff. Voc
| -0.44982 | Temp. Coeff. Voc absolute
| 0.045 | Temp. Coeff. Isc
| 0.019912 | Temp. Coeff. Isc absolute
Regulator info: | 150 | Voc max | 85 | Ibat max
| 55 | Voc min | 48 | System voltage | 18
| 49 | Vmpp min | 0.975 | Max. Efficiency
Voltage drop: | 0.0178 | Cupper resistance
| 0.029667 | Factor
RESULTS:
Temperature | Voc max. | Voc START min. | Vmpp RUN min. | String Voc max. | String Vmpp max. | String Vmpp corr.max. | String Voc min. | String Vmpp min. | String Vmpp corr. min.
-10 | 150 | 55 | 49 | 148.0437 | 123.7437 | 121.222
-5 | 150 | 55 | 49 | 145.7946 | 121.4946 | 118.9729
0 | 150 | 55 | 49 | 143.5455 | 119.2455 | 116.7238
5 | 150 | 55 | 49 | 141.2964 | 116.9964 | 114.4747
55 | 150 | 55 | 49 |  |  |  | 118.8054 | 94.5054 | 92.0994
60 | 150 | 55 | 49 |  |  |  | 116.5563 | 92.2563 | 89.9021
65 | 150 | 55 | 49 |  |  |  | 114.3072 | 90.0072 | 87.705
70 | 150 | 55 | 49 |  |  |  | 112.0581 | 87.7581 | 85.5081
Temperature | Ibat max. | Impp PV max. | System Voltage | Ibat max. @ Impp | Ibat min. @ Impp
-10 | 85 | 40.9531 | 48 | 85
-5 | 85 | 41.0526 | 48 | 85
0 | 85 | 41.1522 | 48 | 85
5 | 85 | 41.2518 | 48 | 85
55 | 85 | 42.2474 | 48 |  | 81.0998
60 | 85 | 42.3469 | 48 |  | 79.3563
65 | 85 | 42.4465 | 48 |  | 77.6037
70 | 85 | 42.5461 | 48 |  | 75.842

## Language (hidden)
V
Pos. | ENGLISH | DUTCH | ESPANGOL | DEUTSCH | FRANCAIS
1 | Module: | Paneel: | Módulo FV: | Modul: | Panneau:
2 | In series: | In serie: | Cuantos módulos? En Serie: | In Reihe: | En serie:
3 | Parallel: | Parallel: | En paralelo: | Parallel: | Parallèle:
4 | Total PV power: | Totale PV vermogen: | Potencia total FV: | PV Leistung insgesamt: | Puissance PV totale:
5 | Wp | Wp | Wp | Wp | Wc
6 | Module temperature: | Paneel temperatuur: | Temp. módulo FV | Modul Temperatur: | Température Paneau:
7 | Min. | Min. | Min. | Min. | Min.
8 | Max. | Max. | Max. | Max. | Max.
9 | Controller: | Regelaar: | Reguladorr: | Regler: | Régulateur:
10 | System voltage: | Systeem spanning: | Voltaje del sistema: | System Spannung: | Tension du système:
11 | Max. input voltage | Max. ingangsspanning | Voltaje max. de entrada | Max. Eingangspannung: | Tension d'entrée max.:
12 | Max. PV voltage @ min. temperature | Max. PV spanning @ min. temp. | Voltaje max. FV @ Temperatura min. | Max. PV Spannung @ min. Temp. | PV tension max. @ temp. min.
13 | Min. input voltage @ MPP | Min. ingangsspanning @ MPP | Voltaje min. de entrada @ PMP | Min. Eingangspannung @ MPP | Tension d'entrée min. @ MPP
14 | Min. PV voltage @ max. temperature | Min. PV spanning @ max. Temp. | Voltaje min. FV @ Temperatura max. | Min. PV Spannung @ max. Temp. | PV tension min. @ temp. max.
15 | Max. output current | Max. uitgangsstroom | Corriente max. de salida | Max. Ausgangstrom | Courant de sortie max.
16 | Max. current @ MPP min. temp. | Max. stroom @ MPP min. temp. | Corriente max. @ PMP temp. min. | Max. Strom @ MPP min. Temp. | Courant max. @ MPP temp. min.
17 | Max. current @ MPP max. temp. | Max. stroom @ MPP max. temp. | Corriente max. @ PMP temp. max. | Max. Strom @ MPP max. Temp. | Courant max. @ MPP temp. max.
18 | Solar module configuration | Zonne-paneel configuratie | Configuración del módulo FV | Solar Modul Auslegung | Configuration du panneau
19 | Example locations with expected temperatures: | Voorbeeld lokaties en verwachte temperatuur: | Ejemplos de lugares con temperaturas previstas: | Beispiel Standort und erwartete Temperatur: | Exemple de localisation de site avec la température attendue:
20 | Flat on mobile home, all year (poor ventilation) | Vlak op camper, gehele jaar (slechte ventilatie) | Plano sobre una autocaravana, durante todo el año (mala ventilación) | Flach auf Wohnmobil, ganze Jahr (schlechte Hinterlüftung) | À plat sur toit de camping-car toute l'année (mauvaise ventilation)
21 | Flat on mobile home, only summer (poor ventilation) | Vlak op camper, alleen zomers (slechte ventilatie) | Plano sobre una autocaravana, sólo en verano (mala ventilación) | Flach auf Wohnmobil, nur Sommer (schlechte Hinterlüftung) | À plat sur camping-car , seulement l'été (mauvaise ventilation)
22 | Flat on boat (poor ventilation) | Vlak op boot (slechte ventilatie) | Plano sobre el techo de un barco (mala ventilación) | Flach auf Boot (schlechte Hinterlüftung) | À plat sur ​​le bateau (mauvaise ventilation)
23 | Pitched on boat (good ventilation) | Onder helling op boot (goede ventilatie) | Inclinado sobre el techo de un barco (buena ventilación) | Geneigt auf Boot (gute Hinterlüftung) | Inclinée sur bateau (bonne ventilation)
24 | Pitched roof in warm region (good ventilation) | Op schuin dak warme omgeving (goede ventilatie) | Techo inclinado en una región cálida (buena ventilación) | Schrägdach, warme Umgebung (gute Hinterlüftung) | Toit en pente, en région chaude (bonne ventilation)
25 | Pitched roof in average region (good ventilation) | Op schuin dak gemiddelde omgeving (goede ventilatie) | Techo inclinado en una región templada (buena ventilación) | Schrägdach, mittlere Regio (gute Hinterlüftung) | Toit en pente, région tempérée (bonne ventilation)
26 | Pitched roof on mountain (good ventilation) | Op schuin dak in de bergen (goede ventilatie) | Techo inclinado en las montañas (buena ventilación) | Schrägdach, in Bergen (gute Hinterlüftung) | Toit en pente, en montagne (bonne ventilation)
27 | * Power limiting @ low temp. | * Vermogens begrenzing @ lage temp. | * Reducción de potencia @ Temp. baja | * Leistung Begrenzung @ niedrige Temp. | * Limitation de puissance @ basse temp.
28 | ** Power limiting @ high temp. | ** Vermogens begrenzing @ hoge temp. | ** Reducción de potencia @ Temp. alta | ** Leistung Begrenzung @ hohe Temp. | ** Limitation de puissance @ haute temp.
29 | Voltage window | Spanningsvenster | Ventana de voltaje | Spannungsfenster | Fourchette de tension
30 | Current window | Stroomvenster | Ventana de corriente | Stromfenster | Fourchette de courant
31 | Cable length, Module to MPPT * | Kabel lengte, paneel tot MPPT * | Largo de cable entre modulo y MPPT * | Kabel Länge, Modul zum MPPT * | Longueur cable, Paneaux à MPPT *
32 | Cross-section: | Doorsnede: | Sección: | Querschnitt: | Section:
33 | * One way length | * Enkele afstand | * Longitud de un solo cable | * Einfache Distanz | * La distance simple
34 | Are the solar modules covered with snow many periods a year? | Zijn de panelen gedurende veel periodes bedekt met sneeuw? | ¿Los módulos están cubiertos con nieve durante muchos períodos del año? | Sind die Solar Module öfters im Jahr bedeckt mit Schnee? | Les panneaux PV sont-ils souvent couverts de neige ?
35 | Yes | Ja | Si | Ja | Oui
36 | No | Nee | No | Nein | Non
37 | Accepted | Toegestaan | Aceptado | Erlaubt | Accepté
38 | NOT accepted | NIET toegestaan | NO aceptado | NICHT erlaubt | PAS accepté

## Version
History
2.0 | - Added the MPPT 75/10 and took out the discontinued 75/50
1.9 | - Added new solar modules, and now 10 additional modules can be added instead of 3.
1.8 | - Added a small calculation on the 'Modules' TAB to help when temperature coefficiences are not in %/°C or %/°K but in mV/°C or mA/°C
1.7 | - Added new solar modules, voltage drop correction and an option to rise the cell temperature in the example list, when the solar modules do not see snow and therefor temperatures will not be so low.
1.6 | - Inserted 4 new regulators and 2 more custom module.
1.5 | - Inserted 4 languages @ updated not applicable (N.A.) voltages for 75/15, 75/50 & 100/15.
1.4 | - Changed texts and Module temperature window.
1.3 | - Power reduction comment set @ highest temperature.
1.2 | - Reduced output current to maximum output current at low & high temperatures. Now a system will show 'power loss' only wenn the output current exceeds the max. at low & high temperatures.
1.1 | - Inserted BlueSolar MPPT 100/15
- Inserted custom module
1.0 | - First version